{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Data"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Data","index":0,"n_rows":6,"n_cols":12,"rows_kept":6,"cut":false,"hidden":false,"merged":[]}
["Базовый расход","Диаметр, м","Уклон","Наполнение","скорость, м/сек","Расход, л/сек","погрешность, %","Угол, град","Площадь, м","Радиус, м","коэффициент  С","коэффициент  шерховатости"]
[10,0.15,5.0000000000000001E-3,0.81000000000000061,{"$f":"ROUND(K2*(J2*C2)^0.5,4) -N(\"Вычисляем скорость вживом сечении \")","v":0.65129999999999999},{"$f":"ROUND(1000*E2*I2,4)","v":9.9649000000000001},{"$f":"100-(F2*100/A2)","v":0.35099999999999909},{"$f":"DEGREES(ACOS(1-2*D2)) -N(\"Находим угол в градусах \")","v":128.31613447366581},{"$f":"ROUND(((PI()*1^2/4-((1/2)^2/2*(PI()*(2*(180-H2)/180)-SIN(2*(180-H2)*PI()/180))))*B2^2),4) -N(\"Вычисляем живое сечение. Формулой: площадь круга минус площадь сегмента \")","v":1.5299999999999999E-2},{"$f":"ROUND(B2*(I2/B2^2)/(PI()*H2/180),4) -N(\"Вычисляем гидравлический радиус, где ПИ*d*угол/180 - смоченный периметр \")","v":4.5499999999999999E-2},{"$f":"ROUND(J2^(2.5*($L$2^0.5)-0.13-($L$2^0.5-0.1)*0.75*J2^0.5)/$L$2,4) -N(\"формула Павловского\")","v":43.181600000000003},1.4E-2]
[12,0.2,5.0000000000000001E-3,0.53000000000000036,{"$f":"ROUND(K3*(J3*C3)^0.5,4) -N(\"Вычисляем скорость вживом сечении \")","v":0.71020000000000005},{"$f":"ROUND(1000*E3*I3,4) -N(\"Вычисляем расход в живом сечении, переводим из кубов в литры \")","v":12.0024},{"$f":"100-(F3*100/A3)","v":-1.9999999999996021E-2},{"$f":"DEGREES(ACOS(1-2*D3)) -N(\"Находим угол в градусах \")","v":93.439812767515235},{"$f":"ROUND(((PI()*1^2/4-((1/2)^2/2*(PI()*(2*(180-H3)/180)-SIN(2*(180-H3)*PI()/180))))*B3^2),4) -N(\"Вычисляем живое сечение. Формулой: площадь круга минус площадь сегмента \")","v":1.6899999999999998E-2},{"$f":"ROUND(B3*(I3/B3^2)/(PI()*H3/180),4) -N(\"Вычисляем гидравлический радиус, где ПИ*d*угол/180 - смоченный периметр \")","v":5.1799999999999999E-2},{"$f":"ROUND(J3^(2.5*($L$2^0.5)-0.13-($L$2^0.5-0.1)*0.75*J3^0.5)/$L$2,4) -N(\"формула Павловского\")","v":44.128900000000002},1.014]
[12,0.2,5.0000000000000001E-3,0.53000000000000036,{"$f":"ROUND(K4*(J4*C4)^0.5,4) -N(\"Вычисляем скорость вживом сечении \")","v":0.71020000000000005},{"$f":"ROUND(1000*E4*I4,4) -N(\"Вычисляем расход в живом сечении, переводим из кубов в литры \")","v":12.0024},{"$f":"100-(F4*100/A4)","v":-1.9999999999996021E-2},{"$f":"DEGREES(ACOS(1-2*D4)) -N(\"Находим угол в градусах \")","v":93.439812767515235},{"$f":"ROUND(((PI()*1^2/4-((1/2)^2/2*(PI()*(2*(180-H4)/180)-SIN(2*(180-H4)*PI()/180))))*B4^2),4) -N(\"Вычисляем живое сечение. Формулой: площадь круга минус площадь сегмента \")","v":1.6899999999999998E-2},{"$f":"ROUND(B4*(I4/B4^2)/(PI()*H4/180),4) -N(\"Вычисляем гидравлический радиус, где ПИ*d*угол/180 - смоченный периметр \")","v":5.1799999999999999E-2},{"$f":"ROUND(J4^(2.5*($L$2^0.5)-0.13-($L$2^0.5-0.1)*0.75*J4^0.5)/$L$2,4) -N(\"формула Павловского\")","v":44.128900000000002},2.0139999999999998]
[12,0.2,5.0000000000000001E-3,0.53000000000000036,0.71020000000000005,12.0024,-1.9999999999996021E-2,93.439812767515235,1.6899999999999998E-2,5.1799999999999999E-2,44.128900000000002,3.0139999999999998]
[12,0.2,5.0000000000000001E-3,0.53000000000000036,0.71020000000000005,12.0024,-1.9999999999996021E-2,93.439812767515235,1.6899999999999998E-2,5.1799999999999999E-2,44.128900000000002,4.0140000000000002]