{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["#6 Автоматы"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"#6 Автоматы","index":0,"n_rows":84,"n_cols":19,"rows_kept":84,"cut":false,"hidden":false,"merged":[[73,1,75,1],[73,2,75,2],[73,3,75,3],[81,1,83,1],[81,2,83,2],[81,3,83,3],[62,1,64,1],[62,2,64,2],[62,3,64,3],[70,1,72,1],[70,2,72,2],[70,3,72,3],[51,1,53,1],[51,2,53,2],[51,3,53,3],[59,1,61,1],[59,2,61,2],[59,3,61,3],[40,1,42,1],[40,2,42,2],[40,3,42,3],[48,1,50,1],[48,2,50,2],[48,3,50,3],[29,1,31,1],[29,2,31,2],[29,3,31,3],[37,1,39,1],[37,2,39,2],[37,3,39,3]]}
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,1,"ЩР 2.1.3"]
[null,2,"*****, L123, ввод ЩР 2.1.3-1","Scheider ic60N","ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",34,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",31,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",32,"0,1",3,"-",5,"+","соответствует"]
[null,5,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",26,"0,1",50,"-",100,"+","соответствует"]
[null,6,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",26,"0,1",50,"-",100,"+","соответствует"]
[null,7,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",36,"0,1",50,"-",100,"+","соответствует"]
[null,8,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",20,"0,1",50,"-",100,"+","соответствует"]
[null,9,"*****, L3, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDС","-",10,10,"50-100",26,"1...60",35,"0,1",50,"-",100,"+","соответствует"]
[null,10,"*****, L123, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDD","-",10,10,"100-200",26,"1...60",37,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",34,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",20,"0,1",100,"-",200,"+","соответствует"]
[null,null,"*****, L123, ввод ЩР 2.1.3-1","Scheider ic60N","ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",28,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",38,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",36,"0,1",3,"-",5,"+","соответствует"]
[null,13,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",27,"0,1",50,"-",100,"+","соответствует"]
[null,14,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",40,"0,1",50,"-",100,"+","соответствует"]
[null,15,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",38,"0,1",50,"-",100,"+","соответствует"]
[null,16,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",21,"0,1",50,"-",100,"+","соответствует"]
[null,17,"*****, L3, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDС","-",10,10,"50-100",26,"1...60",39,"0,1",50,"-",100,"+","соответствует"]
[null,18,"*****, L123, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDD","-",10,10,"100-200",26,"1...60",27,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",31,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",36,"0,1",100,"-",200,"+","соответствует"]
[null,21,"*****, L123, ввод ЩР 2.1.3-1","Scheider ic60N","ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",21,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",32,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",29,"0,1",3,"-",5,"+","соответствует"]
[null,24,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",26,"0,1",50,"-",100,"+","соответствует"]
[null,25,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",33,"0,1",50,"-",100,"+","соответствует"]
[null,26,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",33,"0,1",50,"-",100,"+","соответствует"]
[null,27,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",25,"0,1",50,"-",100,"+","соответствует"]
[null,28,"*****, L3, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDС","-",10,10,"50-100",26,"1...60",25,"0,1",50,"-",100,"+","соответствует"]
[null,29,"*****, L123, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDD","-",10,10,"100-200",26,"1...60",37,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",37,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",32,"0,1",100,"-",200,"+","соответствует"]
[null,32,"*****, L123, ввод ЩР 2.1.3-1","Scheider ic60N","ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",40,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",39,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",24,"0,1",3,"-",5,"+","соответствует"]
[null,35,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",34,"0,1",50,"-",100,"+","соответствует"]
[null,36,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",40,"0,1",50,"-",100,"+","соответствует"]
[null,37,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",25,"0,1",50,"-",100,"+","соответствует"]
[null,38,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",31,"0,1",50,"-",100,"+","соответствует"]
[null,39,"*****, L3, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDС","-",10,10,"50-100",26,"1...60",22,"0,1",50,"-",100,"+","соответствует"]
[null,40,"*****, L123, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDD","-",10,10,"100-200",26,"1...60",40,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",34,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",20,"0,1",100,"-",200,"+","соответствует"]
[null,43,"*****, L123, ввод ЩР 2.1.3-1","Scheider ic60N","ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",32,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",22,"0,1",3,"-",5,"+","соответствует"]
[null,null,null,null,"ОВВ","МDB","-","1","1","2020-03-05",3,"1...60",22,"0,1",3,"-",5,"+","соответствует"]
[null,46,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",36,"0,1",50,"-",100,"+","соответствует"]
[null,47,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",25,"0,1",50,"-",100,"+","соответствует"]
[null,48,"*****, L1, группа ЩР 2.1.3-2","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",20,"0,1",50,"-",100,"+","соответствует"]
[null,49,"*****, L2, группа ЩР 2.1.3-3","Legrand 03389","ОВВ","МDС","-","10","10","50-100",26,"1...60",26,"0,1",50,"-",100,"+","соответствует"]
[null,50,"*****, L3, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDС","-",10,10,"50-100",26,"1...60",28,"0,1",50,"-",100,"+","соответствует"]
[null,51,"*****, L123, группа ЩР 2.1.3-4","Legrand 03389","ОВВ","МDD","-",10,10,"100-200",26,"1...60",26,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",39,"0,1",100,"-",200,"+","соответствует"]
[null,null,null,null,"ОВВ","МDD","-",10,10,"100-200",26,"1...60",40,"0,1",100,"-",200,"+","соответствует"]