{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["2021 г"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"2021 г","index":0,"n_rows":2252,"n_cols":18,"rows_kept":2252,"cut":false,"hidden":false,"merged":[[0,0,0,11],[1,0,1,11]]}
["Выписка диспетчера"]
["из оперативного журнала об аварийных ситуациях __________"]
[null,"Дата","Время","Посёлок","№ Кот.","№ записи","Информация","Дата и время начала работ","Дата и время окончания","дата и время отключения ресурса","кол-во перекрытых аб-в","дата и время подачи ресурса","Маш авар №","Спецтех. марка","наем. /собс.","Прибытие","Убытие","Проведенная работа"]
[{"$f":"IF(B4=\"\",\"\",IF(H4=\"\",1,IF(H4<>\"\",IF(I4=\"\",1,2))))","v":2},"2021-09-10","11:00:00","Беляки","4","564","ул.Октябрьская ТК-30 порыв т.провода т.сети в т.трассе.","2021-09-13T17:00:00","2021-09-14T01:00:00","2021-09-10T21:00:00","2 ж.д","2021-09-14T13:00:00",null,"Исудзу","с","17:00","1:00"]
[2,"2021-09-10","17:30:00","Ангарский","1","569","ул.Береговая ТК-71 порыв трубопровода т.сети в ТК. ","2021-09-13T17:00:00","2021-09-13","2021-09-10","1 ж.д в/з","2021-09-13"]
[2,"2021-09-13","11:20:00","Нижнетерянск","30","585","ул Спортивная 2 порыв т/провода. треб-ся эксковатор. ","2021-09-13T17:00:00","2021-09-15","2021-09-13",8,"2021-09-15",null,"Исудзу","с","15:00","19:00"]
[2,"2021-09-13","11:30:00","Манзя ","29","586","ул Высотского 12 порыв в Т/К-20","2021-09-13T17:00:00","2021-09-13"]
[2,"2021-09-13","12:00:00","Гремучий","20","587","ул Ворошилова Т/К-64 порыв ф-108","2021-09-13T17:00:00","2021-09-13",null,null,null,null,"Исудзу","с","9:00","10:30"]
[2,"2021-09-13","16:30:00","Ангарский","1","590","ул. Береговая в Т/К-69 порыв т/провода. вТ\\К стоит вода.","2021-09-13T17:00:00","2021-09-17","2021-09-13",2,"2021-09-17","Уаз ",null,null,"9:40","18:00"]
[2,"2021-09-13","20:15:00","Гремучий","20","591","ул. Береговая в Т/К-24 порыв т/провода. вТ\\К стоит вода.","2021-09-13T17:00:00","2021-09-14","2021-09-13","2 кв","2021-09-14"]
[2,"2021-09-14","09:00:00","Шиверский","24","597","ул.Лесная 40 порыв т.провода т.сети в т.трассе. Труба ф-108.","2021-09-13T17:00:00","2021-09-18","2021-09-14","17 кв","2021-09-18"]
[2,"2021-09-14","09:50:00","Шиверский","24","598","ул.Ленина ТК-100, между ж/д №36 и №38 порыв т.провода т.сети в т.трассе.","2021-09-13T17:00:00","2021-09-15","2021-09-14","Школа, почта,мед.пункт, 72 кв","2021-09-15",null,"Исудзу","с","12:35","22:00"]
[2,"2021-09-14","10:10:00","Артюгино","3","599","ул.Юбилейная 11 ТК-6, порыв т.провода т.сети в т.трассе. Труба ф-114.","2021-09-13T17:00:00","2021-09-16","2021-09-14","2 кв","2021-09-16",null,"Исудзу","с","8:00","14:00"]
[2,"2021-09-14","11:15:00","Манзя ","28","601","ул.Строителей 5 ТК-8 порыв т.провода т.сети на вводе. Труба ф-32.","2021-09-15","2021-06-16","2021-09-14","1 кв","2021-09-16",null,"Досан","н","11:30","19:00"]
[2,"2021-09-14","12:00:00","Шиверский","24","603","ул.Лесная 30 порыв т.провода т.сети на вводе. Труба ф-32.","2021-09-18","2021-09-18","2021-09-14","12 кв","2021-09-18"]
[2,"2021-09-15","09:00:00","Хребтовый","53","617","порыв т/т от ТК6-ТК7,32 труба.","2021-09-21","2021-09-21","2021-09-15","в/б","2021-09-21",null,"КАМАТСУ","н","8:00","17:50"]
[2,"2021-09-30","11:35:00","Шиверский","24","88","ул.Лесная 30 порыв т.провода т.сети на вводе. Труба ф-32.","2021-09-30","2021-09-30","2021-09-30","13 кв","2021-09-30",null,"исудзу","с"]
[2,"2021-09-15","20:30:00","Шиверский ","23","627","пер Центральный 4 порыв на подводе к дому","2021-09-18","2021-09-18","2021-09-16",1,"2021-09-18"]
[2,"2021-09-15","21:00:00","Ангарский","1","628","пер Пролетарский 4 ТК2 порыв в ТК,лопнула резьба.","2021-09-16","2021-09-16","2021-09-15","1аб","2021-09-16"]
[2,"2021-09-16","19:30:00","Красногорьевский","21","635","ул. Новая 5 порыв т\\сети ф-32","2021-09-18","2021-09-18","2021-09-16","2 кв","2021-09-18"]
[2,"2021-09-20","16:20:00","Красногорьевский","21","652","ул.Новая 6 порыв на вводе ф-32","2021-09-20","2021-09-20"]
[2,"2021-09-20","10:40:00","Артюгино","3","647","ул.Гагарина 10 порыв т\\провода .Требуется эксковатор","2021-09-21","2021-09-21",null,null,null,"Уаз 474 ","Исудзу","с","10:30","14:00"]
[2,"2021-09-20","10:45:00","Артюгино","3","648","ул.Юбилейная 7 порыв т\\провода. ","2021-09-21","2021-09-21",null,null,null,"Уаз 358"]
[2,"2021-09-20","12:00:00","Шиверский","23","649","пер.Центральный 4 порыв т\\провода (воздушка)","2021-09-21","2021-09-21",null,null,null,"Уаз 358 "]
[2,"2021-09-21","08:35:00","Гремучий","20","1","ул.Мира ТК-46, порыв т.провода т.сети.Требуется эксковатор,АВ бригада.","2021-09-21","2021-09-21","2021-09-21","30кв","2021-09-21",null,"Исудзу","с","17:00"]
[2,"2021-09-22","08:50:00","Хребтовый","53","13","пер.Школьный порыв т.провода т.сети между ТК-6 и ТК-7. Труба ф-40","2021-09-23","2021-09-23","2021-09-22","в/б","2021-09-23",null,"Эксковатор","н","11:00","15:00"]
[2,"2021-09-23","09:05:00","Артюгино","3","19","ул Юбилейная 7 порыв т/трассы,труба 76.","2021-09-24","2021-09-24",null,"нет",null,null,"исудзу","с"]
[2,"2021-09-23","10:00:00","Шиверский ","24","20","ул Лесная 18 порыв в ТК10. Нужана труба 25 3м, 2 крана на 25.","2021-09-23","2021-09-23","2021-09-23","2аб","2021-09-23"]
[2,"2021-09-23","14:00:00","Красногорьевский","21","26","ул Набережная 10 порыв на подводе к дому.","2021-09-23","2021-09-23","2021-09-23","1аб","2021-09-23"]
[2,"2021-09-23","17:00:00","Шиверский ","24","29","ул Лесная ТК93 замена задвижек","2021-09-23","2021-09-23","2021-09-23","8аб","2021-09-23"]
[2,"2021-09-24","09:30:00","Шиверский","24",null,"ул.Ленина 13 порыв т/трассы ф-50 ","2021-09-24","2021-09-26","2021-09-24","16 аб-в ШК,почта.","2021-09-25","Уаз 474 ","исудзу","с","25.09.21 11:00","26.09.21 00:10"]
[2,"2021-06-26","10:20:00","Шиверский","24","51","ул.Пушкина порыв т.провода т.сети между Ж/Д  №10 и №12","2021-09-27","2021-09-27","2021-09-26","11 кв"]
[2,"2021-09-27","09:00:00","Хребтовый","53","56","пер.Школьный порыв т.провода т.сети между ТК-6 и ТК-7. Труба ф-40","2021-09-27","2021-09-27","2021-09-27","в/б","2021-09-27","Своими силами","Экскаватор","н","14:30","16:10"]
[2,"2021-09-27","13:00:00","Шиверский","23","60","пер.Центральный 4 порыв т\\провода т.сети в ТК-69. Труба ф-25","2021-09-27","2021-09-27","2021-09-27","33 кв","2021-09-27"]
[2,"2021-09-27","13:10:00","Шиверский","24","61","ул.Пушкина 29 порыв т.провода т.сети в ТК-48. Лопнул сгон ф-25.","2021-09-27","2021-09-27","2021-09-27","23кв","2021-09-27"]
[2,"2021-09-27","14:20:00","Красногорьевский","22","62","ул.Лесная 8 порыв т.провода т.сети на вводе. Труба ф-32.","2021-09-28","2021-09-28",null,"нет"]
[2,"2021-09-27","14:30:00","Артюгино","3","63","ул.Калинина 19 порыв т.провода т.сети на вводе. Труба ф-50.","2021-09-29","2021-09-29","2021-09-27","1 кв","2021-09-29","747","исудзу","с","10:00","14:00"]
[2,"2021-09-27","19:20:00","Шиверский ","24","66","ул Пушкина ТК73 порыв т/трассы,вода посупает со стороны ТК74.","2021-09-28","2021-09-28","2021-09-27","15аб.","2021-09-28"]
[2,"2021-09-28","08:00:00","Артюгино","3","68","ул Юбилейная 7 порыв т/трассы,труба 76.","2021-09-29","2021-09-29",null,"нет",null,"747","Исудзу","с","14:00","15:00"]
[2,"2021-09-28","14:50:00","Шиверский","24",null,"ул. Лесная 48 порыв т/провода по трассе ф-50","2021-09-28","2021-09-28",null,"нет"]
[2,"2021-10-01","09:00:00","Красногорьевский","22","94","ул Лесная ТК69 порыв т/т,устраняем своими силами","2021-10-01","2021-10-01",null,null,null,null,"Исузу","с","9:00","16:15"]
[2,"2021-10-01","17:05:00","Красногорьевский","21","99","ул Ленина 14 порыв на подводе к дому,нужен эксоватор.","2021-10-02","2021-10-02","2021-10-01","7аб","2021-10-02"]
[2,"2021-10-01","18:00:00","Красногорьевский","21","99","ул Ленина 14 порыв на подводе к дому,нужен эксоватор.","2021-10-02","2021-10-02","2021-10-01","7аб","2021-10-02"]
[2,"2021-10-02","08:45:00","Шиверский","24","104","ул. Пушкина 10 порыв т\\провода ф-76","2021-10-02","2021-10-02"]
[2,"2021-10-02","17:30:00","Манзя ","29","108","ул.Молодёжная 12, порыв т.трассы от ТК-10 до ж/д.","2021-10-04","2021-10-04","2021-10-02","2кв.","2021-10-04","Своими силами","в ручную"]
[2,"2021-10-05","10:20:00","Шиверский","24","122","ул Пушкина 8 порыв центральной т/трассы.","2021-10-05","2021-10-05","2021-10-05","9аб","2021-10-05","уаз","исузу","с","15:00","23:00"]
[2,"2021-10-07","08:20:00","Шиверский","23","134","ул.Пушкина ТК-61, порыв центрального т.провода ф-219. ","2021-10-08","2021-10-08","2021-10-08","ост.котел.","2021-10-08",null,"хитачи","с","15:00","17:30"]
[2,"2021-10-07","08:20:00","Шиверский","24","135","ул.Лесная 48, порыв т.провода ,центрального или подвода не ясно.","2021-10-08","2021-10-08","2021-10-08","16 кв","2021-10-08",null,"хитачи","с","12:35"]
[2,"2021-10-09","07:50:00","Шиверский","23","143","ул.Пушкина ТК-61, порыв т.провода т.сети в т.трассе. ф-219. ","2021-10-10","2021-10-10",null,"нет"]
[2,"2021-10-09","11:40:00","Шиверский ","23","145","пер Молодёжный 2 порыв на подводе к дому, труба 32.","2021-10-10","2021-10-10",null,"нет"]
[2,"2021-10-11","07:00:00","Шиверский","24","154","ул.Пушкина 12 порыв т/провода ф-108","2021-10-11","2021-10-11","2021-10-11",9,"2021-10-11",null,"исудзу","с","10:25","15:00"]
[2,"2021-10-11","10:25:00","Шиверский","23","155","ул.Пушкина ТК-61 порыв т.провода т.сети в т.трассе. Труба ф-219.","2021-10-17","2021-10-24","2021-10-23","Котельная останавливалась","2021-10-24","уаз","хитачи","с","11:00","14:00"]
[2,"2021-10-11","18:20:00","Шиверский","24","158","пер.Строительный 2 порыв т.провода т.сети на вводе. Труба ф-32.","2021-10-13","2021-10-13","2021-10-13",20,"2021-10-13",null,"исудзу","н","10:00","15:30"]
[2,"2021-10-12","09:30:00","Ангарский","1","163","ул Спортивная порыв,конкретное место неизвестно.","2021-10-13","2021-10-13",null,"нет"]
[2,"2021-10-13","11:00:00","Ангарский","1","173","Т\\трасса от Котельной воздушка ф-110 порыв ","2021-10-14","2021-10-14",null,"нет"]
[2,"2021-10-14","11:00:00","Красногорьевский","21","181","ул Ангарская 2 в ТК41 стоит вода,порыв т/трассы.","2021-10-14","2021-10-14","2021-10-14","5аб","2021-10-14",null,"Исудзу","с","15:30","00:00"]
[2,"2021-10-14","14:30:00","Шиверский","24","184","ул Лесная 24 порыв подвода к дому.","2021-10-15","1900-01-15","2021-10-14","1аб","2021-10-15"]
[2,"2021-10-16","09:45:00","Шиверский ","24","188","ул Пушкина 28 ТК49 порыв т/трассы.","2021-10-17","2021-10-17","2021-10-16","34аб","2021-10-17"]
[2,"2021-10-19","09:30:00","Шиверский","24","201","ул.Лесная 48, порыв т.провода , ф-32","2021-10-21","2021-10-21",null,"нет"]
[2,"2021-10-20","08:00:00","Красногорьевский","21","207","ул.Ленина 15 порыв т. Провода ф-32","2021-10-20","2021-10-20","2021-10-20",1,"2021-10-20","474","исудзу","с","11:00","20:00"]
[2,"2021-10-21","08:10:00","Артюгино ","3","212","ул Юбилейная 5 ТК16 порыв т/трассы.","2021-10-30","2021-10-30","2021-10-30","Теплосопровождение на водобашню.","2021-10-30","уаз","исудзу","н","9:35","12:00"]
[2,"2021-10-22","10:00:00","Шиверский","24","216","ул Пушкина 10 порыв т/трассы.","2021-10-22","2021-10-22","2021-10-22","13аб","2021-10-22","Уаз","Исудзу","с","13:00","17:00"]
[2,"2021-10-22","10:40:00","Манзя ","28","217","порыв т/трассы от ТК1 в сторону котельной. Труба 159.","2021-10-26","2021-10-26","2021-10-26","21 аб-в","2021-10-26",null,"Исудзу","н","9:00","13:00"]
[2,"2021-10-22","18:00:00","Гремучий","20","218","ул Студенческая 17 порыв т/трассы","2021-10-26","2021-10-26","2021-10-26","2аб-та","2021-10-26"]
[2,"2021-10-23","12:30:00","Шиверский","24","220","ул. Лесная 39 порыв т/провода на вводе ф-32","2021-10-26","2021-10-26","2021-10-26","12аб-в","2021-10-26","УАЗ 358","Исудзу","с","11:40","15:40"]
[2,"2021-10-27","09:00:00","Шиверский","23","239","ул Пушкина ТК61 порыв т/трассы.","2021-10-27","2021-10-27",null,"нет"]
[2,"2021-10-27","09:40:00","Красногорьевский","21","241","ул Ленина ТК12 замена отвода и крана на 20","2021-10-27","2021-10-27","2021-10-27","9аб","2021-10-27"]
[{"$f":"IF(B68=\"\",\"\",IF(H68=\"\",1,IF(H68<>\"\",IF(I68=\"\",1,2))))","v":2},"2021-11-01","10:00:00","Гремучий","20","270","ул.Ворошилова в ТК-68 ,порыв т.провода т.сети.","2021-11-01","2021-11-01",null,"нет"]
[2,"2021-11-02","11:30:00","Шиверский","23","274","ул Пушкина ТК61 побежал байпас в ТК.","2021-11-03","2021-11-03",null,"нет"]
[2,"2021-11-04","07:30:00","Шиверский","23","282","ул. Лесная 4 порыв т\\провода ","2021-11-04","2021-11-04",null,"нет",null,"Т 358 ОУ","Хитачи","с","13:40","1:00"]
[2,"2021-11-04","08:20:00","Гремучий","20","283","ул. Студенческая 17, порыв т.провода т.сети между ТК-4 и ТК-5(Тк без им.)","2021-11-04","2021-11-04",null,"нет"]
[2,"2021-11-04","14:20:00","Шиверский","23","288","ул. Лесная 6 порыв т.провода т.сети в ТК-19 вода.","2021-11-04","2021-11-05","2021-11-04","1аб-т","2021-11-05","Т 358 ОУ","Хитачи","с","14:30","1:00"]
[2,"2021-11-05","14:30:00","Шиверский","23","294","ул Пушкина 4 Контора \"Теплосервис\" порыв т/трассы. Ф-32","2021-11-05","2021-11-08","2021-11-05","перекрыта контора","2021-11-08",null,"Хитачи","с","14:30","20:00"]
[2,"2021-11-08","09:00:00","Ангарский","1","301","ул Береговая ТК71 порыв,в ТК стоит вода.","2021-11-08","2021-11-08","2021-11-08","2 аб","2021-11-08"]
[2,"2021-11-09","07:00:00","Шиверский","24","305","пер Строительный 6-2 порыв теплового сопровождения.","2021-11-09","2021-11-09",null,"нет"]
[2,"2021-11-09","13:30:00","Шиверский","24","311","ул.Ленина 16 порыв т\\трассы ф-108","2021-11-11","2021-11-11","2021-11-11","16аб, школа","2021-11-11",null,"Исудзу","н","11:00","20:00"]
[2,"2021-11-09","10:00:00","Манзя ","25","309","ул. Ангарская 14 порыв т\\трассы ф-50","2021-11-12","2021-11-12","2021-11-09",3,"2021-11-12",null,"ЭксЛАПА","н","15:00","17:00"]
[2,"2021-11-10","10:00:00","Гремучий","20","314","ул.Мира ТК-49, порыв центрального т.провода т.сети ф-150.","2021-11-09","2021-11-12","2021-11-11","70аб-в","2021-11-11",null,"Исудзу","с","9:00","15:00"]
[2,"2021-11-09","10:00:00","Манзя ","25","309","ул.Ангарская 14 порыв т\\трассы т.сети на подводе к дому.","2021-11-15","2021-11-15","2021-11-09",1,"2021-11-15"]
[2,"2021-11-13","12:15:00","Гремучий","20","333","ул.Мира 38, порыв т.спутника на ж/д №38","2021-11-13","2021-11-13"]
[2,"2021-11-13",4.875,"Шиверский","24","335","ул.Лесная от ТК-93 до ТК-10,обнаружен участок порыва т.трассы т.сети.","2021-11-16","2021-11-16","2021-11-16","1 кв","2021-11-16","т 358 оу","исудзу","н","12:00","18:00"]
[2,"2021-11-14","09:00:00","Гремучий","20","339","ул Московская ТК16 порыв т/трассы,150 труба.","2021-11-15","2021-11-15","2021-11-15",30,"2021-11-15"]
[2,"2021-11-14","09:00:00","Гремучий","20","340","ул Мира 42 порыв т/трассы.","2021-11-14","2021-11-14","2021-11-14","50аб","2021-11-14","Уаз","исудзу","с","9:00","21:00"]
[2,"2021-11-16","11:00:00","Гремучий","20","348","ул.Мира ТК-45, между ж/д №32 и №34, порыв т.провода т.сети в т.трассе.","2021-11-16","2021-11-16","2021-11-16","60 кв","2021-11-16",null,"исудзу","с","11:00","22:00"]
[2,"2021-11-17","08:15:00","Шиверский","24","354","ул.Лесная 22, порыв т.провода т.сети подвод ф-32.","2021-11-17","2021-11-17","2021-11-17","1аб-т","2021-11-17",null,"Исудзу","н","14:40","19:00"]
[2,"2021-11-18","13:30:00","Шиверский","23","368","пер Центральный ТК35 порыв в ТК","2021-11-18","2021-11-18","2021-11-18","33аб","2021-11-18"]
[2,"2021-11-18","13:50:00","Шиверский","24","369","ул Пушкина 30 ТК48 порыв т/трассы.","2021-11-19","2021-11-19","2021-11-19",45,"2021-11-19"]
[2,"2021-11-20","11:00:00","Шиверский","24","376","ул.Пушкина 14 порыв спутника тепла на вводе.","2021-11-29","2021-11-29",null,"нет"]
[2,"2021-11-22","13:50:00","Красногорьевский","2","379","ул Ленина 20 ТК13 порыв т/трассы.","2021-11-22","2021-11-22","2021-11-22","2аб","2021-11-22","уаз","Исудзу","с","13:50","17:00"]
[2,"2021-11-24","13:10:00","Беляки","4","384","ул.Школьная ТК-18 порыв т.провода т.сети в ТК. Труба ф-150.","2021-11-25","2021-11-26","2021-11-25","20аб-в ШК,д/сад,СДК,Мед.пункт,Почта.","2021-11-26"]
[2,"2021-11-24","17:30:00","Манзя ","25","385","ул.Береговая 27 порыв т.провода т.сети на вводе. Труба ф-32.","2021-11-27","2021-11-27","2021-11-25","1аб-т","2021-11-27","Уаз 474 ","Исудзу","н","14:00","17:30"]
[2,"2021-11-25","16:00:00","Беляки","4","391","ул.Школьная ТК-27 А порыв т.провода т.сети в ТК. Труба ф-150.","2021-11-25","2021-11-26","2021-11-25","20аб-в ШК,д/сад,СДК,Мед.пункт,Почта.","2002-11-26"]
[2,"2021-11-29","16:30:00","Шиверский","24","400","ул.Пушкина ТК-75 подтекает манометр.(крана для перекрытия нет)","2021-12-01","2021-12-01",null,"нет"]
[2,"2021-11-30","09:30:00","Шиверский","24","405","ул Ленина 16 порыв на подводе к дому,32 труба.","2021-11-30","2021-11-30","2021-11-30","16аб, школа, почта","2021-11-30","уаз","Исудзу","н","16:00","21:00"]
[2,"2021-11-30","09:45:00","Беляки","4","406","ул Школьная 36 ТК20 порыв в ТК.","2021-11-30","2021-11-30","2021-11-30","2аб","2021-11-30"]
[2,"2021-11-30","10:25:00","Артюгино ","3","407","ул Юбилейная 29 ТК10 порыв т/трассы.","2021-12-06","2021-12-06","2021-12-06","8 кв","2021-12-06",null,"исудзу","н","15:30","21:00"]
[2,"2021-11-30","10:30:00","Артюгино","3","408","ул Юбилейная 11 порыв т/трассы.","2021-12-06","2021-12-06","2021-12-06","1 спутник тепла","2021-12-06",null,"исудзу","н","13:00","14:00"]
[2,"2021-12-01","12:30:00","Шиверский","24","411","ул.Ленина 13 порыв т/трассы ф-100 на вводе в школу","2021-12-04","2021-12-04","2021-12-04","16аб, школа и почта","2021-12-04","Уаз","Исудзу","с","11:30","20:00"]
[2,"2021-12-02","08:05:00","Шиверский","24","412","ул.Пушкина 10 порыв т.провода т.сети в т.трассе. Труба ф-108","2021-12-02","03.12.212","2021-12-02","14 кв","2021-12-02",null,"исудзу","с","12:00"]
[2,"2021-12-02","11:30:00","Беляки","4","416","ул.Школьная 27, порыв т.провода т.сети в т.трассе труба ф-32.","2022-01-06","2022-01-06","2022-01-06","1аб","2022-01-06","уаз","Исудзу","с","12:00","17:00"]
[2,"2021-11-03","08:25:00","Манзя ","25","421","ул.Карла Маркса д.2 \"а\" , порыв т.провода на подводе к ж/д, труба ф-32","2021-12-03","2021-12-04","2021-11-03","1аб-т","2021-12-04",null,"экскаватор ЦРКК","н","03.12.21 16:50","03.12.21 17:40"]
[2,"2021-12-06","08:55:00","Артюгино","3","440","ул.Юбилеёная 3, ТК-14 порыв т.провода т.сети в т.трассе. Труба ф-76","2021-12-06","2021-12-06","2021-12-06","нет","2021-12-06",null,"исудзу","н","14:00","15:00"]
[2,"2021-12-07","14:00:00","Шиверский","24","448","ул.Пушкина от ТК-74 до Тк-75,порыв т.провода т.сети,труба ф-108.","2021-12-08","2021-12-08","2021-12-08","59аб","2021-12-08","уаз","Исудзу","с","15:00","22:30"]
[2,"2021-12-07","17:15:00","Шиверский","24","450","ул.Ленина 30 порыв т.провода т.сети в ТК-90 вода.","2021-12-10","2021-12-11","2021-12-10","126 кв","2021-12-10",null,"исудзу","с","12:40","00:00"]
[2,"2021-12-09","16:00:00","Шиверский","24","459","ул. Пушкина 10 порыв т\\провода ф-108 рядом с ТК","2021-12-09","2021-12-09","2021-12-09",13,"2021-12-09"]
[2,"2021-12-10","10:05:00","Шиверский","24","464","ул.Пушкина 10 порыв т.провода т.сети в т.трассе, между ТК-73 и ТК-74.","2021-12-12","2021-12-12",null,"нет"]
[2,"2021-12-10","10:05:00","Шиверский","24","465","ул.Пушкина 27 ТК-49 порыв т.провода т.сети в ТК. Лопнул сгон ф-32.","2021-12-11","2021-12-12",null,"нет",null,"Т 358 ОУ"]
[2,"2021-12-10","22:50:00","Шиверский","24","467","ул.Пушкина 16 порыв т.провода т.сети между ТК-55 и ТК-56.Труба ф-108.","2021-12-11","2021-12-11","2021-12-11","14аб-в","2021-12-11","Т 358 ОУ","Исудзу 056 ","с","13:00","20:00"]
[2,"2021-12-11","20:00:00","Шиверский","24","472","ул.Пушкина отТК-48 до Тк-49, порыв т.провода т.сети труба ф-108,","2021-12-11","2021-11-12","2021-12-11","49аб-в","2021-11-12","Т 358 ОУ","Исудзу 056 ","с","20:00","4:00"]
[2,"2021-12-12","15:00:00","Шиверский","24","480","пер Комсомольский 1 порыв на подводе к дому.","2021-12-12","2021-12-12","2021-12-12","1аб-т","2021-12-12","Уаз 474 ","Исудзу","н","16:00"]
[2,"2021-12-13","06:00:00","Шиверский","24","481","ул Пушкина между 24 и 26 порыв т/трассы.","2021-12-13","2021-12-13","2021-12-13","36аб","2021-12-13"]
[2,"2021-12-13","07:30:00","Шиверский","24","482","ул Береговая 7 ТК43-ТК92 порыв т/трассы.","2021-12-14","2021-12-15","2021-12-14","3аб ","2021-12-15",null,"хендай","н","17:15","21:45"]
[2,"2021-12-13","14:30:00","Шиверский","24",null,"ул. Пушкина 16  порыв т\\сети","2021-12-13","2021-12-13"]
[2,"2021-12-14","11:20:00","Шиверский","24","490","ул.Пушкина 18 порыв т.провода т.сети на вводе в дом. Труба ф-32.","2021-12-17","2021-12-17","2021-12-14","2 кв","2021-12-17",null,"исудзу","с","15:00"]
[2,"2021-12-15","17:20:00","Шиверский","24","498","ул Пушкина 8 порыв в воздушке. ТК-74 -75","2021-12-17","2021-12-17","2021-12-15","1аб","2021-12-17"]
[2,"2021-12-16","07:00:00","Шиверский","24","500","ул Береговая между 8-9 домом порыв т/трассы.","2021-12-16","2021-12-17","2021-12-16",3,"2021-12-16"]
[2,"2021-12-17","08:15:00","Манзя ","25","505","ул.Береговая порыв т.провода т.сети от ТК-68 до ТК-73. Труба ф-89.","2021-12-28","2021-12-28","2021-12-28","5аб-в","2021-12-28",null,"исудзу","н","14:30","17:00"]
[2,"2021-12-18","08:00:00","Шиверский","24","506","ул Пушкина 10 порыв т/трассы.","2021-12-18","2021-12-18","2021-12-18","14аб-в","2021-12-18","Уаз","Исудзу","с","12:30","21:00"]
[2,"2021-12-19","07:20:00","Шиверский","24","510","ул Пушкина 16 порыв т/трассы.","2021-12-26","2021-12-26",null,"нет"]
[2,"2021-12-19","13:00:00","Шиверский","23","512","ул.Лесная 5 порыв на вводе","2021-12-19","2021-12-20",null,"нет"]
[2,"2021-12-20","12:05:00","Шиверский","23","517","ул.Лесная 9 порыв т.провода т.сети в т.трассе.","2021-12-25","2021-12-25","2021-12-25","19аб","2021-12-25","уаз","Исудзу","н","15:30","18:00"]
[2,"2021-12-20","16:10:00","Н.Терянск","30","519","ул.Молодёжная порыв т.провода т.сети в т.трассе от ТК-3 до ТК-44.","2021-12-23","2021-12-23","2021-12-23","ост.котел.","2021-12-23",null,"исудзу","н","12:30","18:20"]
[2,"2021-12-21","14:30:00","Шиверский","24","523","ул Лесная 40 порыв т.провода т.сети в т.трассе","2021-12-25","2021-12-25","2021-12-25","14аб-в","2021-12-25","уаз","Исудзу","н","10:00","15:30"]
[2,"2021-12-22","08:00:00","Шиверский","24","525","ул Пушкина 10 между ТК74-ТК75 порыв т/трассы,вышла вода.","2021-12-22","2021-12-23","2021-12-23",14,"2021-12-23"]
[2,"2021-12-23","21:00:00","Шиверский","24","532","ул.Пушкина 12 порыв т.провода т.сети в т.трассе. В ТК-73 вода.","2021-12-23","2021-12-27",null,"нет"]
[2,"2021-12-24","09:45:00","Шиверский","24","535","ул.Пушкина 10, порыв т.провода т.сети в т.трассе.Вышла вода между","2021-12-25","2021-12-25","2021-12-25","14аб-в","2021-12-25","уаз","Исудзу","н","10:00","18:00"]
[2,"2021-12-26","08:00:00","Шиверский","24","550","ул.Пушкина 14 порыв спутника тепла на вводе.","2021-12-26","2021-12-26",null,"нет"]
[2,"2021-12-26","11:00:00","Манзя ","25","551","ул Первомайская 20 порыв на вводе ф-32","2021-12-28","2021-12-28","2021-12-28","13 аб-в","2021-12-28",null,"исудзу","н","12:00","14:30"]
[2,"2021-12-27","09:40:00","Ангарский","1","556","ул.Береговая порыв т.провода подпитки с в/з, между ТК-69 и ТК-71.","2021-12-29","2021-12-29",null,"нет",null,null,"Исудзу","н","9:30","9:40"]
[2,"2021-12-27","10:05:00","Шиверский","23","557","пер.Молодёжный 2 порыв т.провода т.сети в т.трассе. Труба ф-108.","2021-12-31","2021-12-31","2021-12-31","8 кв","2021-12-31",null,"экскаватор\nкитаец","с","9:30","12:30"]
[2,"2021-12-27","13:50:00","Шиверский","24","559","ул.Пушкина в ТК-55, побежал сливник,подкручивали,воду не держит.","2022-01-10","2022-01-10","2022-01-10","57 аб","2022-01-10","уаз"]
[{"$f":"IF(B132=\"\",\"\",IF(H132=\"\",1,IF(H132<>\"\",IF(I132=\"\",1,2))))","v":2},"2021-12-27","16:05:00","Шиверский","24","560","ул.Лесная 38 порыв т.провода т.сети в центральной т.трассе. Труба ф-83.","2021-12-30","2021-12-30","2021-12-30",16,"2021-12-30"]
[2,"2021-12-27","16:05:00","Шиверский","23","561","ул.Ленина 13 порыв т.провода т.сети в центральной т.трассе.Труба ф-150.","2021-12-31","2021-12-31","2021-12-31","8 кв+ школа, почта","2021-12-31",null,"экскаватор\nкитаец","с","13:00","15:30"]
[2,"2021-12-27","16:05:00","Шиверский","23","562","ул.Ленина 16 порыв т.провода т.сети в т.трассе. Труба ф-133.","2021-12-30","2021-12-30","2021-12-30",10,"2021-12-30"]
[2,"2021-12-31","22:40:00","Шиверский","24","18","ул.Пушкина порыв т.провода т.сети между Ж/Д  №10 и №12","2022-01-01","2022-01-01",null,"нет"]
[2,"2022-01-06","13:30:00","Ангарский","1","41","ул Октябрьская 16 ТК33 побежал вентель","2022-01-07","2022-01-07","2022-01-07",60,"2022-01-07"]
[2,"2022-01-07","07:00:00","Артюгино","3","44","ул Юбилейная 7 порыв т/трассы.","2022-01-12","2022-01-12",null,"нет"]
[2,"2022-01-07","07:00:00","Артюгино","3","45","ул Юбилейная 3 порыв т/трассы.","2022-01-11","2022-01-12",null,"нет"]
[2,"2022-01-07","14:00:00","Шиверский","24","47","ул Пушкина 10 порыв т/трассы.","2022-01-10","2022-01-10","2022-01-10","14аб-в","2022-01-10","уаз","Хитачи","с","14:00","16:30"]
[2,"2022-01-10","10:30:00","Красногорьевский","21","56","ул Октябрьская ТК26 порыв т/трассы,труба на 100.","2022-01-10","2022-01-10","2022-01-10","30аб","2022-01-10","уаз","Исудзу","с","14:00","19:00"]
[2,"2022-01-10","11:30:00","Шиверский","24","57","ул Пушкина ТК53 замена задвижки ф- 100 по обратке","2022-01-10","2022-01-10","2022-01-10","57 аб","2022-01-10"]
[2,"2022-01-10","11:30:00","Шиверский","24","58","ул Пушкина ТК48 замена 1 крана, 2 сгонов ф- 32 по подаче.","2022-01-10","2022-01-10","2022-01-10","57аб","2022-01-10"]
[2,"2022-01-11","00:30:00","Шиверский","24","63","ул Пушкина 10 порыв т/трассы.","2022-01-11","2022-01-12","2022-01-11","14 аб","2022-01-11"]
[2,"2022-01-11","17:00:00","Артюгино","64","3","ул Гагарина 10 порвы Т\\трассы","2022-01-12","2022-01-12",null,"нет",null,null,null,"с","15:00","17:00"]
[2,"2022-01-14","22:00:00","Шиверский","24","84","ул Береговая 7 порыв центральной т/т, труба на 50.","2022-01-15","2022-01-15",null,"нет"]
[2,"2022-01-18","09:30:00","Шиверский","24",null,"ул Пушкина 10 порыв т/трассы.","2022-01-18","18:01.22"]
[2,"2022-01-18","17:00:00","Шиверский","24",null,"ул.Береговая 8 порыв т\\трассы.","2022-01-18","2022-01-18"]
[2,"2022-01-19","09:05:00","Хребтовый","53","98","пер. Школьный ТК-5 порыв в ТК отвод на школу, труба ф-76.","2022-01-30","2022-01-30",null,"нет"]
[2,"2022-01-19","11:00:00","Шиверский","23","99","ул Ленина ТК34 установка байпаса на 50.","2022-01-19","2022-01-19","2022-01-19","20аб, школа, дет сад, почта.","2022-01-19","уаз"]
[2,"2022-01-21","09:10:00","Шиверский","23","102","ул.Береговая 1,порыв спутника тепла.","2022-01-23","2022-01-23","2022-01-21","1спутник"]
[2,"2022-01-21","15:10:00","Шиверский","24","109","ул.Пушкина 10,потыв т.трассы ,в ТК-74 вода.","2022-01-21","2022-01-21","2022-01-21","14аб-в","2022-01-21","358"]
[2,"2022-01-21","20:10:00","Шиверский","24","112","ул. Береговая 7, порыв центральной т.трассы т.сети, вода вышла наружу.","2022-01-27","2022-01-27",null,"нет"]
[2,"2022-01-22","08:00:00","Ангарский","1",null,"ул Красноармейская порвы т\\трассы","2022-01-22","2022-01-22",null,"нет"]
[2,"2022-01-22","16:00:00","Ангарский","1","114","ул Октябрская порыв т\\трассы около школы","2022-01-22","2022-01-22",null,"нет"]
[2,"2022-01-23","01:30:00","Ангарский","1","115","ул.Краснормейская  около котелной порыв на помещение диз гена.","2022-01-23","2022-01-23","2022-01-23","помещение диз гена","2022-01-23"]
[2,"2022-01-23","14:25:00","Артюгино","3","116","ул. Юбилейная 7 порыв т/трассы,труба ф-76.","2022-01-25","2022-01-25","2022-01-25","1аб-т","2022-01-25","474","Исудзу","с","25.01.22","25.01.22"]
[2,"2022-01-23","14:30:00","Артюгино","3","117","ул. Юбилейная 25 порыв на вводе в клуб сразу после фундамента(у абонента)","2022-01-24","2022-01-25","2022-01-24","клуб(половина здания)","2022-01-25","474","исудзу","с","25.01.22","25.01.22"]
[2,"2022-01-24","09:50:00","Шиверский","24","121","ул.Ленина ТК -26 неисправна задвижка на обратном трубопроводе ф-150.","2022-01-24","2022-01-25","2022-01-24","43 аб-в","2022-01-24"]
[2,"2022-01-24","10:35:00","Н.Терянск","30","122","ул.Юности порыв спутника тепла от ТК-23 до ТК-15. Ф-159.","2022-01-24","2022-01-24","2022-01-24","спутник тепла"]
[2,"2022-01-26","08:00:00","Артюгино","3","141","ул.Юбилейная д.9 порыв центр. Т.трассы, вода вышла наружу.ф-76.","2022-01-29","2022-01-29","2022-01-29","Теплосопровождение","2022-01-29","358","Исудзу","с","29.01.22","29.01.22"]
[2,"2022-01-26","08:30:00","Шиверский","24","142","пер Комсомольский 1 порыв на подводе к дому.","2022-01-28","2022-01-28","2022-01-28","2 кв","2022-01-28",null,"исудзу","с","12:45","16:00","Вскрыли 3 м т.трассы, Заменили 3м трубы и 1 отвод, ф-32, обратка, закопали т.трассу."]
[2,"2022-01-26","10:30:00","Артюгино","3","144","ул. Юбилейная между ТК-1 ТК-9 порыв т/т,труба ф-100.","2022-01-29","2022-01-29",null,"нет"]
[2,"2022-10-26","12:00:00","Шиверский","24","145","ул Пушкина 10 порыв т/трассы.","2022-01-27","2022-01-27",null,"нет"]
[2,"2022-01-26","15:00:00","Шиверский","24","147","ул Пушкина 18 порыв на подводе к дому.","2022-01-28","2022-01-28","2022-01-28","2 кв","2022-01-28",null,"исудзу","с","16:05","18:40","Вскрыли 4 м т.траасы, заменили 3,5м трубы и 1 отвод, ф-40, обратка. Закопали т.трассу."]
[2,"2022-01-28","11:20:00","Шиверский","24","150","ул.Лесная 40 порыв т.провода т.сети в т.трассе. Труба ф-83.","2022-01-28","2022-01-28","2022-01-28","15 кв","2022-01-28",null,"экскаватор","н","13:05","16:00","Вскрыли 6 м т.трассы, заменили 2 м трубы, ф-40, обратка. Закопали т.трассу."]
[2,"2022-01-29","03:00:00","Н.Терянск","30","153","Перемёрз трубопровод со скважины. Работают на подпитке ЦРКК","2022-02-15","2022-02-15"]
[2,"2022-01-30","11:00:00","Манзя ","25","161","ул Ленина ТК24 направление на гараж с/а,труба на 50.","2022-01-31","2022-01-31",null,"нет"]
[2,"2022-02-01","10:40:00","Шиверский","24","168","ул.Пушкина 10 порыв т.провода т.сети в т.трассе. Труба ф-108","2022-02-02","2021-02-04","4,02.21",13,"2021-02-04"]
[2,"2022-02-02","09:00:00","Шиверский","24","169","ул.Лесная 23,порыв т.провода т.сети,оторвало сгон ф-32, обратка.","2022-02-22","2022-02-22","2022-02-22","8 аб-в","2022-02-22","УАЗ","Исудзу","с","22.02.22","22.02.22"]
[2,"2022-02-02","15:00:00","Шиверский","24","171","пер.Комсомольский д2, порыв спутника тепла от 01.02.22.","2022-02-08","2022-02-08","2022-02-08",34,"2022-02-08",null,null,null,null,null,"отключили спутник х/в"]
[2,"2022-02-05","10:00:00","Гремучий","20","182","ул.Мира 56 порыв т.провода т.сети на вводе.","2022-02-05","2022-02-05","2022-02-05","1 кв","2022-02-05"]
[2,"2022-02-06","14:00:00","Шиверский","23","192","ул.Лесная 3,порыв т.провода т.сети ,в  ТК-18 вода.","2022-02-07","2022-02-07","2022-02-07","19 аб","2022-02-07","Уаз 474 ","Исдзу","с","11:00","19:00","Расскопали и закопали 5м т/трассы."]
[2,"2022-02-15","13:00:00","Гремучий ","20","212","ул Московская 34 порыв на подводе к дому.","2022-02-15","2022-02-15","2022-02-15","40аб","2022-02-15","Уаз 474 ","Исудзу","с","13:00","19:00","Расскопали и закопали 3м т/т."]
[2,"2022-02-21","08:10:00","Артюгино","3","224","ул.Калинина 19 порыв т.провода т.сети в ТК-13. Труба ф-100.","2022-02-21","2022-02-21","2022-02-21","4кв,ФАП,клуб","2022-02-21","474"]
[1,"2022-02-21","10:15:00","Гремучий","20","225 ","ул.Ворошилова в ТК-67 порыв т.провода т.сети.","2022-02-22",null,null,"нет",null,"358","Исудзу","с","10:00","21:00","Вскрыли 3 плиты,Место порыва не уточнено.Работы перенесены на 24.02"]
[2,"2022-02-25","08:50:00","Хребтовый","53","239","ул.Школьная порыв т.провода т.сети в ТК-5.","2022-02-25","2022-02-25","2022-02-25","ост.котел.","2022-02-25","474","нет"]
[1,"2022-02-25","18:25:00","Шиверский","24","240","ул.Пушкина 16 ТК-56 порыв т.провода т.сети в т.трассе. Труба ф-108.",null,null,null,"нет"]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B196=\"\",\"\",IF(H196=\"\",1,IF(H196<>\"\",IF(I196=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B260=\"\",\"\",IF(H260=\"\",1,IF(H260<>\"\",IF(I260=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B324=\"\",\"\",IF(H324=\"\",1,IF(H324<>\"\",IF(I324=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B388=\"\",\"\",IF(H388=\"\",1,IF(H388<>\"\",IF(I388=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B452=\"\",\"\",IF(H452=\"\",1,IF(H452<>\"\",IF(I452=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B516=\"\",\"\",IF(H516=\"\",1,IF(H516<>\"\",IF(I516=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B580=\"\",\"\",IF(H580=\"\",1,IF(H580<>\"\",IF(I580=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(#REF!=\"\",\"\",IF(#REF!=\"\",1,IF(#REF!<>\"\",IF(#REF!=\"\",1,2))))","v":{"$error":"#REF!"}}]
[{"$f":"IF(B595=\"\",\"\",IF(H595=\"\",1,IF(H595<>\"\",IF(I595=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B659=\"\",\"\",IF(H659=\"\",1,IF(H659<>\"\",IF(I659=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B723=\"\",\"\",IF(H723=\"\",1,IF(H723<>\"\",IF(I723=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B787=\"\",\"\",IF(H787=\"\",1,IF(H787<>\"\",IF(I787=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B851=\"\",\"\",IF(H851=\"\",1,IF(H851<>\"\",IF(I851=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B915=\"\",\"\",IF(H915=\"\",1,IF(H915<>\"\",IF(I915=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B979=\"\",\"\",IF(H979=\"\",1,IF(H979<>\"\",IF(I979=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1043=\"\",\"\",IF(H1043=\"\",1,IF(H1043<>\"\",IF(I1043=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1107=\"\",\"\",IF(H1107=\"\",1,IF(H1107<>\"\",IF(I1107=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1171=\"\",\"\",IF(H1171=\"\",1,IF(H1171<>\"\",IF(I1171=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1235=\"\",\"\",IF(H1235=\"\",1,IF(H1235<>\"\",IF(I1235=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1299=\"\",\"\",IF(H1299=\"\",1,IF(H1299<>\"\",IF(I1299=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1363=\"\",\"\",IF(H1363=\"\",1,IF(H1363<>\"\",IF(I1363=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1427=\"\",\"\",IF(H1427=\"\",1,IF(H1427<>\"\",IF(I1427=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1491=\"\",\"\",IF(H1491=\"\",1,IF(H1491<>\"\",IF(I1491=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1555=\"\",\"\",IF(H1555=\"\",1,IF(H1555<>\"\",IF(I1555=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1619=\"\",\"\",IF(H1619=\"\",1,IF(H1619<>\"\",IF(I1619=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1683=\"\",\"\",IF(H1683=\"\",1,IF(H1683<>\"\",IF(I1683=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1747=\"\",\"\",IF(H1747=\"\",1,IF(H1747<>\"\",IF(I1747=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1811=\"\",\"\",IF(H1811=\"\",1,IF(H1811<>\"\",IF(I1811=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1875=\"\",\"\",IF(H1875=\"\",1,IF(H1875<>\"\",IF(I1875=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B1939=\"\",\"\",IF(H1939=\"\",1,IF(H1939<>\"\",IF(I1939=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B2003=\"\",\"\",IF(H2003=\"\",1,IF(H2003<>\"\",IF(I2003=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B2067=\"\",\"\",IF(H2067=\"\",1,IF(H2067<>\"\",IF(I2067=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B2131=\"\",\"\",IF(H2131=\"\",1,IF(H2131<>\"\",IF(I2131=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[{"$f":"IF(B2195=\"\",\"\",IF(H2195=\"\",1,IF(H2195<>\"\",IF(I2195=\"\",1,2))))","v":""}]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]
[""]